## README
NERC supply data - Week 1 Early Warning Dashboard
Purpose | Clean, tidy tables from three NERC reports so a supply-side early warning dashboard can be built and every total traced back to the report.
Sources | NERC 2025 Annual Report; NERC Quarterly Report Q1 2026 (covers 2025/Q4 vs 2026/Q1); NERC Quarterly Report Q2 2026 (covers 2026/Q1 vs 2026/Q2). All three PDFs came from NERC_REPORTS.zip.
Quarters covered | 2025/Q4, 2026/Q1, 2026/Q2. The files contain no quarterly plant or DisCo tables for 2025 Q1-Q3; the Annual Report only has yearly tables and monthly charts for those months.
Sheet: Plants | One row per plant (28 plants). Installed MW, Hydro/Thermal type, and generation per quarter pulled from Plant_Quarter by formula.
Sheet: Plant_Quarter | One row per plant per quarter (84 rows). Blue cells are numbers copied from NERC Table 1 (availability) and Table 2 (generation). Black cells are formulas.
Sheet: DisCo_Quarter | One row per DisCo per quarter (33 rows). From NERC's DisCo Energy Offtake Performance table (Table 4 in the Q1 report, Table 3 in the Q2 report). 'PH' is Port Harcourt as written in the reports.
Sheet: National_Quarter | The report's own national totals for each quarter (blue) next to values calculated here (black).
Sheet: Monthly | Monthly national available capacity and average hourly generation, typed from the chart data labels (Figures A and B in the Q1 and Q2 reports). Labels are rounded to whole numbers.
Sheet: System_Events | System collapses: 2025 (Annual Report Table 25) and 2026 Q1 (Q1 report Table 3). The Q2 report states there were none.
Sheet: Checks | Reconciliation: this workbook's totals against the totals NERC states, with PASS or FAIL. The tolerance cell can be changed.
Units | MW = capacity (available or installed). MWh/h = average hourly energy, numerically the same as average MW. GWh = quarterly total = MWh/h x 24 x days / 1,000. PAF and load percentages are on a 0-100 scale, as in the reports.
Colour code | Blue text = number typed from a report. Black = formula. Green = link to another sheet. Yellow fill = assumption to confirm.
Assumption 1 | Alaoji_1 shows '-' for 2026/Q1 generation in the Q2 report (not available for dispatch). It is entered as 0, which matches the 0.00 in the Q1 report.
Assumption 2 | Hydro/Thermal type is not a column in the reports. The five plants set as Hydro (Kainji_1, Jebba_1, Shiroro_1, Zungeru_1, Dadin-Kowa_1) are the ones whose combined generation change matches NERC's stated hydro change. See the Checks sheet.
Assumption 3 | 'Generation / Available (%)' in Plant_Quarter is my own ratio (generation divided by available capacity). It is not NERC's official load factor.
Known gaps | (a) The 2025 collapse remarks in the Annual Report PDF are not clearly aligned to one event, so cause for 10/09/2025 is left for you to confirm on page 154. (b) Monthly 2025 Jan-Sep values are chart-only in the Annual Report and are not included.
Verified at build | The 2026/Q1 columns in the Q2 report are identical to the 2026/Q1 columns in the Q1 report for all 28 plants and all 11 DisCos, so no restated figures were found.

## Plants
Plant | Installed capacity (MW) | Type | Generation 2025/Q4 (MWh/h) | Generation 2026/Q1 (MWh/h) | Generation 2026/Q2 (MWh/h) | Change Q1 to Q2 (MWh/h) | Change Q4 to Q1 (MWh/h)
Ihovbor_2 | 461 | Thermal | 402.46 | 419.74 | 419.48 | -0.26 | 17.28
Ikeja_1 | 110 | Thermal | 90.79 | 81.46 | 90.26 | 8.8 | -9.33
Jebba_1 | 578 | Hydro | 405.91 | 400.09 | 363.32 | -36.77 | -5.82
Kainji_1 | 760 | Hydro | 544.2 | 528.02 | 409.44 | -118.58 | -16.18
Okpai_1 | 480 | Thermal | 246.14 | 237.28 | 219.85 | -17.43 | -8.86
Dadin-Kowa_1 | 40 | Hydro | 33.74 | 17.05 | 19.25 | 2.2 | -16.69
Shiroro_1 | 600 | Hydro | 281.79 | 269.58 | 270.61 | 1.03 | -12.21
Zungeru_1 | 700 | Hydro | 440.17 | 280.68 | 314.02 | 33.34 | -159.49
Igbafo_1 | 45 | Thermal | 17.95 | 10.29 | 14.84 | 4.55 | -7.66
Afam_2 | 650 | Thermal | 135.57 | 184.29 | 291.27 | 106.98 | 48.72
Delta_1 | 900 | Thermal | 306.65 | 343.44 | 365.29 | 21.85 | 36.79
Omotosho_1 | 335 | Thermal | 82 | 79.78 | 135.18 | 55.4 | -2.22
Olorunsogo_1 | 335 | Thermal | 88.84 | 83.08 | 136.33 | 53.25 | -5.76
Egbin_1 | 1320 | Thermal | 584.27 | 518.01 | 470.94 | -47.07 | -66.26
Geregu_2 | 435 | Thermal | 80.89 | 98.26 | 81.46 | -16.8 | 17.37
Odukpani_1 | 625 | Thermal | 126.59 | 133.23 | 119.47 | -13.76 | 6.64
Omoku_1 | 150 | Thermal | 33.45 | 27.89 | 28.44 | 0.55 | -5.56
Ihovbor_1 | 500 | Thermal | 19.32 | 54.25 | 61.37 | 7.12 | 34.93
Omotosho_2 | 500 | Thermal | 22.19 | 26.98 | 58.68 | 31.7 | 4.79
Trans Amadi_1 | 100 | Thermal | 7.82 | 9.95 | 21.55 | 11.6 | 2.13
Ibom power_1 | 190 | Thermal | 1.5 | 5.15 | 11.85 | 6.7 | 3.65
Olorunsogo_2 | 750 | Thermal | 46.97 | 103.94 | 53.85 | -50.09 | 56.97
Rivers_1 | 180 | Thermal | 44.74 | 2.04 | 8.88 | 6.84 | -42.7
Alaoji_1 | 500 | Thermal | 0 | 0 | 14.32 | 14.32 | 0
Sapele_2 | 500 | Thermal | 73.66 | 42.86 | 3.46 | -39.4 | -30.8
Afam_1 | 726 | Thermal | 95.03 | 58.42 | 25.72 | -32.7 | -36.61
Sapele Steam_1 | 720 | Thermal | 19.16 | 14.59 | 11.17 | -3.42 | -4.57
Geregu_1 | 435 | Thermal | 220.9 | 82.38 | 2.11 | -80.27 | -138.52
Total | 13625 |  | 4452.7 | 4112.73 | 4022.41 | -90.32 | -339.97

## Plant_Quarter
Plant | Quarter | Type | Installed capacity (MW) | Average available capacity (MW) | PAF reported (%) | Average hourly generation (MWh/h) | PAF recalculated (%) | PAF difference (pp) | Generation / Available (%)
Ihovbor_2 | 2025/Q4 | Thermal | 461 | 441.68 | 95.81 | 402.46 | 95.8091 | -0.00088937 | 91.1203
Ihovbor_2 | 2026/Q1 | Thermal | 461 | 453.95 | 98.47 | 419.74 | 98.4707 | 0.00071584 | 92.4639
Ihovbor_2 | 2026/Q2 | Thermal | 461 | 459.4 | 99.65 | 419.48 | 99.6529 | 0.0029284 | 91.3104
Ikeja_1 | 2025/Q4 | Thermal | 110 | 110 | 100 | 90.79 | 100 | 0 | 82.5364
Ikeja_1 | 2026/Q1 | Thermal | 110 | 107.48 | 97.71 | 81.46 | 97.7091 | -0.00090909 | 75.7908
Ikeja_1 | 2026/Q2 | Thermal | 110 | 108.97 | 99.06 | 90.26 | 99.0636 | 0.0036364 | 82.8301
Jebba_1 | 2025/Q4 | Hydro | 578 | 538.42 | 93.15 | 405.91 | 93.1522 | 0.0022491 | 75.3891
Jebba_1 | 2026/Q1 | Hydro | 578 | 417.78 | 72.28 | 400.09 | 72.2803 | 0.00027682 | 95.7657
Jebba_1 | 2026/Q2 | Hydro | 578 | 400.5 | 69.29 | 363.32 | 69.2907 | 0.00065744 | 90.7166
Kainji_1 | 2025/Q4 | Hydro | 760 | 572.7 | 75.36 | 544.2 | 75.3553 | -0.0047368 | 95.0236
Kainji_1 | 2026/Q1 | Hydro | 760 | 539.37 | 70.97 | 528.02 | 70.9697 | -0.00026316 | 97.8957
Kainji_1 | 2026/Q2 | Hydro | 760 | 429.25 | 56.48 | 409.44 | 56.4803 | 0.00026316 | 95.385
Okpai_1 | 2025/Q4 | Thermal | 480 | 277.06 | 57.72 | 246.14 | 57.7208 | 0.00083333 | 88.84
Okpai_1 | 2026/Q1 | Thermal | 480 | 265.1 | 55.23 | 237.28 | 55.2292 | -0.00083333 | 89.5058
Okpai_1 | 2026/Q2 | Thermal | 480 | 261.84 | 54.55 | 219.85 | 54.55 | 0 | 83.9635
Dadin-Kowa_1 | 2025/Q4 | Hydro | 40 | 33.5 | 83.74 | 33.74 | 83.75 | 0.01 | 100.7164
Dadin-Kowa_1 | 2026/Q1 | Hydro | 40 | 17 | 42.5 | 17.05 | 42.5 | 0 | 100.2941
Dadin-Kowa_1 | 2026/Q2 | Hydro | 40 | 20.24 | 50.59 | 19.25 | 50.6 | 0.01 | 95.1087
Shiroro_1 | 2025/Q4 | Hydro | 600 | 382.58 | 63.76 | 281.79 | 63.7633 | 0.0033333 | 73.6552
Shiroro_1 | 2026/Q1 | Hydro | 600 | 297.08 | 49.51 | 269.58 | 49.5133 | 0.0033333 | 90.7432
Shiroro_1 | 2026/Q2 | Hydro | 600 | 290.91 | 48.48 | 270.61 | 48.485 | 0.005 | 93.0219
Zungeru_1 | 2025/Q4 | Hydro | 700 | 700 | 100 | 440.17 | 100 | 0 | 62.8814
Zungeru_1 | 2026/Q1 | Hydro | 700 | 314.42 | 44.92 | 280.68 | 44.9171 | -0.0028571 | 89.2691
Zungeru_1 | 2026/Q2 | Hydro | 700 | 328.52 | 46.93 | 314.02 | 46.9314 | 0.0014286 | 95.5863
Igbafo_1 | 2025/Q4 | Thermal | 45 | 19.24 | 42.75 | 17.95 | 42.7556 | 0.0055556 | 93.2952
Igbafo_1 | 2026/Q1 | Thermal | 45 | 16.92 | 37.61 | 10.29 | 37.6 | -0.01 | 60.8156
Igbafo_1 | 2026/Q2 | Thermal | 45 | 21.11 | 46.92 | 14.84 | 46.9111 | -0.0088889 | 70.2984
Afam_2 | 2025/Q4 | Thermal | 650 | 135.72 | 20.88 | 135.57 | 20.88 | 0 | 99.8895
Afam_2 | 2026/Q1 | Thermal | 650 | 206.27 | 31.73 | 184.29 | 31.7338 | 0.0038462 | 89.3441
Afam_2 | 2026/Q2 | Thermal | 650 | 294.23 | 45.27 | 291.27 | 45.2662 | -0.0038462 | 98.994
Delta_1 | 2025/Q4 | Thermal | 900 | 435.76 | 48.42 | 306.65 | 48.4178 | -0.0022222 | 70.3713
Delta_1 | 2026/Q1 | Thermal | 900 | 375.68 | 41.74 | 343.44 | 41.7422 | 0.0022222 | 91.4182
Delta_1 | 2026/Q2 | Thermal | 900 | 401.03 | 44.56 | 365.29 | 44.5589 | -0.0011111 | 91.0879
Omotosho_1 | 2025/Q4 | Thermal | 335 | 89.91 | 26.84 | 82 | 26.8388 | -0.001194 | 91.2023
Omotosho_1 | 2026/Q1 | Thermal | 335 | 84.11 | 25.11 | 79.78 | 25.1075 | -0.0025373 | 94.852
Omotosho_1 | 2026/Q2 | Thermal | 335 | 143.76 | 42.91 | 135.18 | 42.9134 | 0.0034328 | 94.0317
Olorunsogo_1 | 2025/Q4 | Thermal | 335 | 89.67 | 26.77 | 88.84 | 26.7672 | -0.0028358 | 99.0744
Olorunsogo_1 | 2026/Q1 | Thermal | 335 | 83.14 | 24.82 | 83.08 | 24.8179 | -0.0020896 | 99.9278
Olorunsogo_1 | 2026/Q2 | Thermal | 335 | 136.53 | 40.75 | 136.33 | 40.7552 | 0.0052239 | 99.8535
Egbin_1 | 2025/Q4 | Thermal | 1320 | 631.11 | 47.81 | 584.27 | 47.8114 | 0.0013636 | 92.5782
Egbin_1 | 2026/Q1 | Thermal | 1320 | 540.96 | 40.98 | 518.01 | 40.9818 | 0.0018182 | 95.7575
Egbin_1 | 2026/Q2 | Thermal | 1320 | 521.44 | 39.5 | 470.94 | 39.503 | 0.0030303 | 90.3153
Geregu_2 | 2025/Q4 | Thermal | 435 | 106.34 | 24.45 | 80.89 | 24.446 | -0.004023 | 76.0673
Geregu_2 | 2026/Q1 | Thermal | 435 | 115.68 | 26.59 | 98.26 | 26.5931 | 0.0031034 | 84.9412
Geregu_2 | 2026/Q2 | Thermal | 435 | 102.64 | 23.6 | 81.46 | 23.5954 | -0.0045977 | 79.3648
Odukpani_1 | 2025/Q4 | Thermal | 625 | 142.39 | 22.78 | 126.59 | 22.7824 | 0.0024 | 88.9037
Odukpani_1 | 2026/Q1 | Thermal | 625 | 141.41 | 22.63 | 133.23 | 22.6256 | -0.0044 | 94.2154
Odukpani_1 | 2026/Q2 | Thermal | 625 | 128.25 | 20.52 | 119.47 | 20.52 | 0 | 93.154
Omoku_1 | 2025/Q4 | Thermal | 150 | 33.76 | 22.51 | 33.45 | 22.5067 | -0.0033333 | 99.0818
Omoku_1 | 2026/Q1 | Thermal | 150 | 30.27 | 20.18 | 27.89 | 20.18 | 0 | 92.1374
Omoku_1 | 2026/Q2 | Thermal | 150 | 30.5 | 20.33 | 28.44 | 20.3333 | 0.0033333 | 93.2459
Ihovbor_1 | 2025/Q4 | Thermal | 500 | 34.44 | 6.89 | 19.32 | 6.888 | -0.002 | 56.0976
Ihovbor_1 | 2026/Q1 | Thermal | 500 | 65.5 | 13.1 | 54.25 | 13.1 | 0 | 82.8244
Ihovbor_1 | 2026/Q2 | Thermal | 500 | 81.68 | 16.34 | 61.37 | 16.336 | -0.004 | 75.1347
Omotosho_2 | 2025/Q4 | Thermal | 500 | 41.11 | 8.22 | 22.19 | 8.222 | 0.002 | 53.9771
Omotosho_2 | 2026/Q1 | Thermal | 500 | 30.73 | 6.15 | 26.98 | 6.146 | -0.004 | 87.7969
Omotosho_2 | 2026/Q2 | Thermal | 500 | 81.38 | 16.28 | 58.68 | 16.276 | -0.004 | 72.1062
Trans Amadi_1 | 2025/Q4 | Thermal | 100 | 5.41 | 5.41 | 7.82 | 5.41 | 0 | 144.5471
Trans Amadi_1 | 2026/Q1 | Thermal | 100 | 8.41 | 8.41 | 9.95 | 8.41 | 0 | 118.3115
Trans Amadi_1 | 2026/Q2 | Thermal | 100 | 15.21 | 15.21 | 21.55 | 15.21 | 0 | 141.6831
Ibom power_1 | 2025/Q4 | Thermal | 190 | 4.11 | 2.16 | 1.5 | 2.1632 | 0.0031579 | 36.4964
Ibom power_1 | 2026/Q1 | Thermal | 190 | 5.08 | 2.67 | 5.15 | 2.6737 | 0.0036842 | 101.378
Ibom power_1 | 2026/Q2 | Thermal | 190 | 24.03 | 12.65 | 11.85 | 12.6474 | -0.0026316 | 49.3134
Olorunsogo_2 | 2025/Q4 | Thermal | 750 | 64 | 8.53 | 46.97 | 8.5333 | 0.0033333 | 73.3906
Olorunsogo_2 | 2026/Q1 | Thermal | 750 | 113.8 | 15.17 | 103.94 | 15.1733 | 0.0033333 | 91.3357
Olorunsogo_2 | 2026/Q2 | Thermal | 750 | 83.02 | 11.07 | 53.85 | 11.0693 | -0.00066667 | 64.8639
Rivers_1 | 2025/Q4 | Thermal | 180 | 54.89 | 30.49 | 44.74 | 30.4944 | 0.0044444 | 81.5085
Rivers_1 | 2026/Q1 | Thermal | 180 | 3.68 | 2.05 | 2.04 | 2.0444 | -0.0055556 | 55.4348
Rivers_1 | 2026/Q2 | Thermal | 180 | 12.35 | 6.86 | 8.88 | 6.8611 | 0.0011111 | 71.9028
Alaoji_1 | 2025/Q4 | Thermal | 500 | 0 | 0 | 0 | 0 | 0 | 0
Alaoji_1 | 2026/Q1 | Thermal | 500 | 0 | 0 | 0 | 0 | 0 | 0
Alaoji_1 | 2026/Q2 | Thermal | 500 | 23.2 | 4.64 | 14.32 | 4.64 | 0 | 61.7241
Sapele_2 | 2025/Q4 | Thermal | 500 | 99.92 | 19.98 | 73.66 | 19.984 | 0.004 | 73.719
Sapele_2 | 2026/Q1 | Thermal | 500 | 52.24 | 10.45 | 42.86 | 10.448 | -0.002 | 82.0444
Sapele_2 | 2026/Q2 | Thermal | 500 | 16.8 | 3.36 | 3.46 | 3.36 | 0 | 20.5952
Afam_1 | 2025/Q4 | Thermal | 726 | 110.68 | 15.24 | 95.03 | 15.2452 | 0.0051791 | 85.8601
Afam_1 | 2026/Q1 | Thermal | 726 | 71.91 | 9.91 | 58.42 | 9.905 | -0.0050413 | 81.2404
Afam_1 | 2026/Q2 | Thermal | 726 | 20.91 | 2.88 | 25.72 | 2.8802 | 0.00016529 | 123.0033
Sapele Steam_1 | 2025/Q4 | Thermal | 720 | 20.74 | 2.88 | 19.16 | 2.8806 | 0.00055556 | 92.3819
Sapele Steam_1 | 2026/Q1 | Thermal | 720 | 19.26 | 2.67 | 14.59 | 2.675 | 0.005 | 75.7529
Sapele Steam_1 | 2026/Q2 | Thermal | 720 | 14.03 | 1.95 | 11.17 | 1.9486 | -0.0013889 | 79.6151
Geregu_1 | 2025/Q4 | Thermal | 435 | 225.24 | 51.78 | 220.9 | 51.7793 | -0.00068966 | 98.0732
Geregu_1 | 2026/Q1 | Thermal | 435 | 80.72 | 18.56 | 82.38 | 18.5563 | -0.0036782 | 102.0565
Geregu_1 | 2026/Q2 | Thermal | 435 | 2.44 | 0.56 | 2.11 | 0.56092 | 0.00091954 | 86.4754

## DisCo_Quarter
DisCo | Quarter | Energy offtake (MWh/h) | Available PCC (MWh/h) | Offtake performance reported (%) | Offtake performance recalculated (%) | Difference (pp)
Abuja | 2025/Q4 | 576.75 | 605.85 | 95.2 | 95.1968 | -0.0031691
Abuja | 2026/Q1 | 550.78 | 553.01 | 99.6 | 99.5968 | -0.0032477
Abuja | 2026/Q2 | 520.26 | 589.31 | 88.28 | 88.2829 | 0.0029071
Benin | 2025/Q4 | 353.04 | 353.04 | 100 | 100 | 0
Benin | 2026/Q1 | 276.96 | 280.82 | 98.62 | 98.6255 | 0.005454
Benin | 2026/Q2 | 262.99 | 275.48 | 95.46 | 95.4661 | 0.0060955
Eko | 2025/Q4 | 480.78 | 500.72 | 96.02 | 96.0177 | -0.0022655
Eko | 2026/Q1 | 445.26 | 452.73 | 98.35 | 98.35 | 9.9397e-06
Eko | 2026/Q2 | 430.21 | 456.51 | 94.24 | 94.2389 | -0.0011005
Enugu | 2025/Q4 | 315.06 | 317.02 | 99.38 | 99.3817 | 0.0017425
Enugu | 2026/Q1 | 262.94 | 264.72 | 99.33 | 99.3276 | -0.0024086
Enugu | 2026/Q2 | 248.95 | 260.73 | 95.48 | 95.4819 | 0.0019162
Ibadan | 2025/Q4 | 433.23 | 459.11 | 94.36 | 94.363 | 0.0030067
Ibadan | 2026/Q1 | 387.44 | 391.58 | 98.94 | 98.9427 | 0.0027448
Ibadan | 2026/Q2 | 374.66 | 397.12 | 94.34 | 94.3443 | 0.0042788
Ikeja | 2025/Q4 | 531.04 | 562.27 | 94.45 | 94.4457 | -0.0042711
Ikeja | 2026/Q1 | 533.42 | 533.42 | 100 | 100 | 0
Ikeja | 2026/Q2 | 507.59 | 527.79 | 96.17 | 96.1727 | 0.0027202
Jos | 2025/Q4 | 185.08 | 219.79 | 84.21 | 84.2077 | -0.0023472
Jos | 2026/Q1 | 173.71 | 183.74 | 94.54 | 94.5412 | 0.0011995
Jos | 2026/Q2 | 162.76 | 169.34 | 96.11 | 96.1143 | 0.0043262
Kaduna | 2025/Q4 | 183.5 | 250.02 | 73.39 | 73.3941 | 0.0041285
Kaduna | 2026/Q1 | 174.53 | 207.77 | 84 | 84.0015 | 0.0015402
Kaduna | 2026/Q2 | 173.01 | 188.18 | 91.94 | 91.9386 | -0.0014305
Kano | 2025/Q4 | 199.89 | 258.29 | 77.39 | 77.3898 | -0.0002443
Kano | 2026/Q1 | 168.95 | 188.28 | 89.73 | 89.7334 | 0.0033758
Kano | 2026/Q2 | 198.5 | 203.72 | 97.44 | 97.4377 | -0.0023405
PH | 2025/Q4 | 284.12 | 291.04 | 97.62 | 97.6223 | 0.00232
PH | 2026/Q1 | 256.43 | 257.7 | 99.51 | 99.5072 | -0.0028211
PH | 2026/Q2 | 247.42 | 252.92 | 97.82 | 97.8254 | 0.0053993
Yola | 2025/Q4 | 76.72 | 109 | 70.38 | 70.3853 | 0.0053211
Yola | 2026/Q1 | 79.06 | 94.25 | 83.88 | 83.8833 | 0.0032891
Yola | 2026/Q2 | 70.7 | 77.3 | 91.47 | 91.4618 | -0.008163

## National_Quarter
Quarter | Days in quarter | Installed capacity reported (MW) | Avg available capacity reported (MW) | PAF reported (%) | Avg hourly generation reported (MWh/h) | Total generation reported (GWh) | DisCo offtake reported (MWh/h) | DisCo PCC reported (MWh/h) | DisCo offtake reported (GWh) | Total generation calculated (GWh) | Generation minus DisCo offtake (MWh/h) | DisCo offtake as % of generation
2025/Q4 | 92 | 13625 | 5400.38 | 39.64 | 4452.71 | 9831.58 | 3619.21 | 3926.15 | n/a | 9831.5837 | 833.5 | 81.2811
2026/Q1 | 90 | 13625 | 4457.96 | 32.72 | 4112.72 | 8883.47 | 3309.48 | 3408.02 | 7148.47 | 8883.4752 | 803.24 | 80.4694
2026/Q2 | 91 | 13625 | 4454.17 | 32.69 | 4022.4 | 8784.93 | 3197.03 | 3398.41 | 6982.32 | 8784.9216 | 825.37 | 79.4807
Notes
Days: 92, 90 and 91 are the day counts NERC states in its report footnotes. DisCo offtake in GWh was not stated for 2025/Q4 in the Q1 report extract, so it shows n/a.
Column L is the gap between what the plants generated and what the DisCos took at their trading points. The tables do not explain this gap, so treat it as a question to investigate.

## Monthly
Month | Quarter | Avg available capacity (MW) | Avg hourly generation (MWh/h) | Generation / Available (%)
Oct-25 | 2025/Q4 | 5506 | 4290 | 77.915
Nov-25 | 2025/Q4 | 5544 | 4701 | 84.7944
Dec-25 | 2025/Q4 | 5151 | 4367 | 84.7797
Jan-26 | 2026/Q1 | 4901 | 4421 | 90.2061
Feb-26 | 2026/Q1 | 4384 | 4102 | 93.5675
Mar-26 | 2026/Q1 | 4089 | 3815 | 93.2991
Apr-26 | 2026/Q2 | 4286 | 4048 | 94.447
May-26 | 2026/Q2 | 4587 | 4128 | 89.9935
Jun-26 | 2026/Q2 | 4489 | 3892 | 86.7008
Source: chart data labels, Figure A and Figure B in the Q1 2026 report (Oct-25 to Mar-26) and the Q2 2026 report (Jan-26 to Jun-26). Labels are rounded to whole numbers, so quarter averages differ slightly from the reported quarterly figures.
Quarter average check (simple average of the three months):
2025/Q4 |  | 5400.3333 | 4452.6667
2026/Q1 |  | 4458 | 4112.6667
2026/Q2 |  | 4454 | 4022.6667

## System_Events
Date | Quarter | Type | Time of collapse (as reported) | Restoration (as reported) | Cause (short summary) | Source
2025-09-10 | 2025/Q3 | Full | 11:20Hrs | 10/09/2025 11:48Hrs | Cause not clearly tied to this event in the PDF layout. Check page 154 of the Annual Report. | Annual Report 2025, Table 25
2025-12-29 | 2025/Q4 | Partial | 14:01Hrs | 29/12/2025 14:30Hrs | Remarks text in the PDF mentions a failed circuit breaker on the Benin-Onitsha 330kV line at Benin station. Confirm on page 154 which event it belongs to. | Annual Report 2025, Table 25
2026-01-23 | 2026/Q1 | Total | 12:40Hrs | not stated | Busbar separation at Sapele transmission station cut the evacuation lines in the Delta corridor, then generation was lost and frequency decayed. | Q1 2026 report, Table 3
2026-01-27 | 2026/Q1 | Partial | 10.48Hrs (as printed) | not stated | Preliminary observation: not enough reactive power to hold voltage margins. | Q1 2026 report, Table 3
none | 2026/Q2 | none | n/a | n/a | The Q2 report states there were no system disturbances on the National Grid. | Q2 2026 report, Summary
Annual Report Table 24 counts collapses per year (2019-2025). 2025: 1 partial and 1 total. The 10/09/2025 event is listed as 'Full' in Table 25 but 'Total' in the Table 24 category.

## Checks
Reconciliation against the totals stated in the reports
Tolerance | 0.02 | Rounding in the reports causes differences up to about 0.01. A bigger gap means a data entry error. Change this cell to test a stricter or looser limit.
Tolerance for 'change' checks | 0.05 | Used for generation-change rows only. Each change sums up to 28 rounded plant values, so rounding can build up. Every individual plant change here is within 0.01 of the printed value.
Check | This workbook | Report states | Difference | Result
Installed capacity, sum of 28 plants (MW) | 13625 | 13625 | 0 | PASS
2025/Q4 available capacity, sum of plants (MW) | 5400.38 | 5400.38 | 0 | PASS
2026/Q1 available capacity, sum of plants (MW) | 4457.95 | 4457.96 | 0.01 | PASS
2026/Q2 available capacity, sum of plants (MW) | 4454.17 | 4454.17 | 0 | PASS
2025/Q4 average hourly generation, sum of plants (MWh/h) | 4452.7 | 4452.71 | 0.01 | PASS
2026/Q1 average hourly generation, sum of plants (MWh/h) | 4112.73 | 4112.72 | 0.01 | PASS
2026/Q2 average hourly generation, sum of plants (MWh/h) | 4022.41 | 4022.4 | 0.01 | PASS
2025/Q4 PAF recalculated from totals (%) | 39.6358 | 39.64 | 0.0041835 | PASS
2026/Q1 PAF recalculated from totals (%) | 32.7189 | 32.72 | 0.0011009 | PASS
2026/Q2 PAF recalculated from totals (%) | 32.6912 | 32.69 | 0.001156 | PASS
2025/Q4 total generation from MWh/h x 24 x days (GWh) | 9831.5837 | 9831.58 | 0.00368 | PASS
2026/Q1 total generation from MWh/h x 24 x days (GWh) | 8883.4752 | 8883.47 | 0.0052 | PASS
2026/Q2 total generation from MWh/h x 24 x days (GWh) | 8784.9216 | 8784.93 | 0.0084 | PASS
2025/Q4 DisCo offtake, sum of 11 DisCos (MWh/h) | 3619.21 | 3619.21 | 0 | PASS
2026/Q1 DisCo offtake, sum of 11 DisCos (MWh/h) | 3309.48 | 3309.48 | 0 | PASS
2026/Q2 DisCo offtake, sum of 11 DisCos (MWh/h) | 3197.05 | 3197.03 | 0.02 | PASS
2025/Q4 DisCo PCC, sum of 11 DisCos (MWh/h) | 3926.15 | 3926.15 | 0 | PASS
2026/Q1 DisCo PCC, sum of 11 DisCos (MWh/h) | 3408.02 | 3408.02 | 0 | PASS
2026/Q2 DisCo PCC, sum of 11 DisCos (MWh/h) | 3398.4 | 3398.41 | 0.01 | PASS
2026/Q1 DisCo offtake in GWh from MWh/h x 24 x days | 7148.4768 | 7148.47 | 0.0068 | PASS
2026/Q2 DisCo offtake in GWh from MWh/h x 24 x days | 6982.3135 | 6982.32 | 0.00648 | PASS
2025/Q4 row count in Plant_Quarter (expect 28 plants) | 28 | 28 | 0 | PASS
2026/Q1 row count in Plant_Quarter (expect 28 plants) | 28 | 28 | 0 | PASS
2026/Q2 row count in Plant_Quarter (expect 28 plants) | 28 | 28 | 0 | PASS
2025/Q4 row count in DisCo_Quarter (expect 11 DisCos) | 11 | 11 | 0 | PASS
2026/Q1 row count in DisCo_Quarter (expect 11 DisCos) | 11 | 11 | 0 | PASS
2026/Q2 row count in DisCo_Quarter (expect 11 DisCos) | 11 | 11 | 0 | PASS
Hydro generation change Q1 to Q2 (MWh/h) | -118.78 | -118.79 | 0.01 | PASS
Thermal generation change Q1 to Q2 (MWh/h) | 28.46 | 28.47 | 0.01 | PASS
Hydro generation change Q4 to Q1 (MWh/h) | -210.39 | -210.38 | 0.01 | PASS
Thermal generation change Q4 to Q1 (MWh/h) | -129.58 | -129.61 | 0.03 | PASS
Plants with lower generation, Q1 to Q2 (report: 12) | 12 | 12 | 0 | PASS
Plants with higher generation, Q1 to Q2 (report: 16) | 16 | 16 | 0 | PASS
Total generation change Q1 to Q2 (MWh/h) | -90.32 | -90.32 | 0 | PASS
Total generation change Q4 to Q1 (MWh/h) | -339.97 | -339.99 | 0.02 | PASS
Checks passed | 35
Checks failed | 0